{"text_format":"3","workbook":"xls","n_sheets":2,"sheets":["技术要求","Sheet2"],"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"技术要求","index":0,"n_rows":46,"n_cols":10,"rows_kept":46,"merged":[[0,0,0,4],[1,7,12,7],[1,9,12,9],[3,4,4,4],[12,0,13,0],[12,4,16,4],[14,0,15,0],[18,1,18,4],[25,0,27,0],[25,1,25,4],[26,2,26,4],[27,2,27,4],[28,2,28,4],[29,2,29,4],[34,0,34,4]],"flags":["formulas_cached_only"]}
["七厂二线除湿机组参数及要求",{"$nulls":4},"七厂二线配组机技术要求","七厂二线分选机技术要求","七厂二线扫码装盆机","七厂二线套膜机"," 七厂二线自动清洗涂油机"]
["序号","名称","项目数据","项目数据","备注","送料方式：托盘式",null,"电芯扫码，装16位托盘，扫码率98%以上，装托盘无阻滞现象，空托盘必须自动送料，配套喷码线必须有下料斗自动下料，须与托盘式配组机联机","材质：能套PET","清洗与涂油独立，保证烘干效果，效率：150PPM以上"]
[1,"除湿区域","二期组装","一期组装改造部份",null,"连接功能：可与扫码装盆机联机使用",null,null,"效率：70PPM以上"]
[2,"处理风量","28000*2",7000,"此项为参考值，具体风量可根据不同厂家的技术方案进行合理的调整。","电压测量范围：0-20VDC","电压测量范围：0-20VDC",null,"能与清洗机连接功能"]
[3,"换气次数","30-40","30-40",null,"电压测量解析度：正负0.1MV","电压测量解析度：正负0.1MV"]
[4,"面积","66500mm*10000mm","3500mm*10000mm",null,"内阻测量范围：0-3.0000Ω","内阻测量范围：0-3.0000Ω"]
[5,"房间高度","2800mm","2800mm",null,"内阻测量解析度：正负0.1MΩ","内阻测量解析度：正负0.1MΩ"]
[6,"人员",35,35,null,"效率：150PPM","效率：200PPM"]
[7,"冗余设计",{"v":0.2,"d":"20%"},{"v":0.2,"d":"20%"},null,"电压、电阻测量CGK:≥1.0","电压、电阻测量CGK:≥1.0"]
[8,"湿度","小于1%","小于1%",null,"数据：数据可保持、查看、拷贝，以便分析","数据：数据可保持、查看、拷贝，以便分析"]
[9,"温度","小于25度","小于25度",null,"通讯：具备MES联网功能，可无线通讯","通讯：具备MES联网功能，可无线通讯"]
[10,"净化","动态10万级","动态10万级",null,null,"分档：18档"]
[11,"机组装机功率",null,null,"厂家务必根据方案提供具体准确的数据给我司，以配备配套的配电箱及电缆",null,"具备喷码功能"]
[null,"机组用电功率"]
[12,"冷冻机装机功率"]
[null,"冷冻机用电功率"]
[13,"总用电功率KW"]
[14,"机组报价（万元）"]
[null,"材料要求"]
[15,"墙、顶材料","0.425玻镁彩钢板","0.425玻镁彩钢板"]
[16,"不锈钢双开门风淋门","1200*2000（物料门）",null,"门页为不锈钢门"]
[17,"不锈钢单开门风淋门","7500*2000（人员）",null,"门页为不锈钢门"]
[18,"照明","LED洁净平板灯净化灯，与一期相同","LED洁净平板灯净化灯，与一期相同"]
[19,"双层中空玻璃","必须严格检查玻璃内部是否干净","必须严格检查玻璃内部是否干净"]
[20,"转轮成分","硅胶/分子筛1：2复合转轮"]
[21,"其它要求"]
[null,"完工工期（交钥匙）","其它要求"]
[null,"天","1、风淋门口配温湿度显示仪2个，包括改造一期，探测头与风淋门口距离为25米，\n2、除湿机组配1个露点仪；\n3、注液区及激光焊区，各配1台排风机及管道；\n4、对以上要求分项报价。\n5、工控原器件统一用欧姆龙品牌，并提供相配套的软件程序，所有的软件不可设定密码。"]
[22,"净化报价（万元）"]
[23,"总报价（万元）"]
[]
[null,"注：此表为低露点除湿机组"]
[]
[]
["除湿机主件及电器原器件品牌"]
["序号","名   称","规格","品牌","备注"]
[1]
[2]
[3]
[4]
[5]
[6]
[7]
[8]
[9]
[10]

{"sheet":"Sheet2","index":1,"n_rows":13,"n_cols":6,"rows_kept":13,"merged":[[1,3,12,3],[1,5,12,5]],"flags":["formulas_cached_only"]}
[null,"七厂二线配组机技术要求","七厂二线分选机技术要求","七厂二线扫码装盆机","七厂二线套膜机"," 七厂二线自动清洗涂油机"]
[null,"送料方式：托盘式",null,"电芯扫码，装16位托盘，扫码率98%以上，装托盘无阻滞现象，空托盘必须自动送料，配套喷码线必须有下料斗自动下料，须与托盘式配组机联机","材质：能套PET","清洗与涂油独立，保证烘干效果，效率：150PPM以上"]
[null,"连接功能：可与扫码装盆机联机使用",null,null,"效率：70PPM以上"]
[null,"电压测量范围：0-20VDC","电压测量范围：0-20VDC",null,"能与清洗机连接功能"]
[null,"电压测量解析度：正负0.1MV","电压测量解析度：正负0.1MV"]
[null,"内阻测量范围：0-3.0000Ω","内阻测量范围：0-3.0000Ω"]
[null,"内阻测量解析度：正负0.1MΩ","内阻测量解析度：正负0.1MΩ"]
[null,"效率：150PPM","效率：200PPM"]
[null,"电压、电阻测量CGK:≥1.0","电压、电阻测量CGK:≥1.0"]
[null,"数据：数据可保持、查看、拷贝，以便分析","数据：数据可保持、查看、拷贝，以便分析"]
[null,"通讯：具备MES联网功能，可无线通讯","通讯：具备MES联网功能，可无线通讯"]
[null,null,"分档：18档"]
[null,null,"具备喷码功能"]